Hazard Resources

The structure of the training software could be something like:

- Hydrogen fundamentals ( this can be our homepage/landing page)

- Flammability and ignition

- Pressure systems (low vs high)

- Leak detection and response

- Ventilation and dispersion

- Fire risks (invisible and autoignition flame jets)

- Emergency procedures

- Application-specific risks (lab, transport, cryogenics)

H2O2 ratios for ignition:

- All fires require 3 things:

  - A fuel (in this case H2)

  - An oxidiser (in this case O2)

  - An ignition source

- H2 has a large flammability range in air, with concentration of ~4-75% allowing for combustion

- <4% leads to a H2 concentration that is too lean to ignite while >75% is too rich

- The stoichiometric ratio for ideal ignition is where the ratio of H2 to O2 in the air matches that of the ratio for complete combustion 2H2+O2->2H2O

  - This corresponds to ~30% H2 in air

  - This results in the fastest flame speed, the maximum energy released and the highest explosion pressure

- The most dangerous time when hydrogen leaks from a source is during mixing, where the ~4-75% H2 concentration is most likely to occur

H2 sensor identification:

- Look for small devices labelled “H₂ detector” , “Hydrogen sensor” or “Gas detector”

- They are often connected with alarm beacons and sirens

- Labs with sensors installed typically have control panels near the entrances that show a gas detection panel, gas concentration levels and/or alarm status

- Signage such as “Hydrogen in use” or “Gas detection system installed” may be present on the lab entrance door

- Hydrogen detectors are mounted high-up or on the ceiling directly

  - This is because hydrogen is 14x lighter than air, meaning it will gather at the highest points in an enclosed space

- Other common mounting points include directly above equipment utilising hydrogen, above storage devices and above electrolysers

- The most effective way to locate H2 detectors is to visually scan the lab ceiling or ask the lab manager about their locations

High pressure vs low pressure:

Hydrogen is typically compressed at varying pressures to enable continuous supply. Storage pressure brackets can be broken down as follows:

- Low pressure

  - <20 bar

  - Typically seen in lab experiments, fuel cell test setups, and electrolyser outputs prior to compression

  - Lower risk profile due to a lower amount of stored energy in a tank, quick dispersal of leaks and a leak lower autoignition risk

  - Key hazards include accumulation in confined spaces and flame/explosion risk

- Medium pressure

  - 20-350 bar

  - Typically seen in industrial gas systems, pre-compression storage chambers

  - Higher risk due to increased amount of stored energy, potential for significant jet release with autoignition and equipment rupture risk

  - Key hazards include those above plus explosive equipment failure

- High pressure

  - 350-750 bar

  - Typically seen in hydrogen vehicle storage systems (passenger =700 bar, heavy duty/truck = 350 bar), high pressure storage tanks and hydrogen refuelling stations

  - High risk profile due to high amount of stored energy, potential high-velocity jet leaks with autoignition and risk of explosive equipment failure

  - Key hazards include those above plus hydrogen embrittlement of storage equipment

Training Scenarios:

- Hydrogen stored at low pressure in a lab

  - Hazard: Hydrogen accumulation in an enclosed space

    - Identification:

      - Hydrogen sensor(s) alarm sounding

      - Little/no ventilation in the lab

      - Hissing sound coming from storage device

      - Unexpected/unexplained pressure drop in storage device

    - Mitigation:

      - Ensure ventilation measures (windows, fume hood, vent fans) are active/open in the lab

      - Regular inspection of hydrogen storage devices by noting pressures

      - Regular inspection of fittings and pipes for leaks by spraying with soapy water

      - Evacuation protocols in place if leak is detected without knowledge of concentration in air

- Hydrogen stored at high pressure in a lab

  - Hazard: Hydrogen accumulation in an enclosed space, tank rupture, high-velocity jet release leading to fire/explosion due to autoignition

    - Identification:

      - Look for storage devices labelled as high pressure (350/700 bar)

      - Look for storage devices fitted with pressure relief devices

      - Use thermal imaging devices to identify leak jets

      - See training scenario 1 above

    - Mitigation:

      - See training scenario 1 above

      - Inspect tanks for any damage to the outer fiberglass layers

      - Notify lab custodian if any tank damage is observed even if no hydrogen leaks are detected

      - Sound alarm and evacuate immediately if hissing is heard due to the ability of high-pressure hydrogen leaks to auto-ignite

- Invisible hydrogen flame in the lab due to leak

  - Hazard: Risk of walking into a hydrogen flame due to its near invisibility in daylight

    - Identification:

      - Heat shimmer in air

      - Roaring sound

      - The use of thermal imaging cameras

      - Automated IR flame detectors in the lab sounding an alert

    - Mitigation:

      - Automated IR flame detectors in the lab

      - If a suspected leak is to be approached, it must be done cautiously and preferably with the use of a thermal imaging camera

      - Include remote shutoff systems in the hydrogen storage system design

- Hydrogen accumulation detected in an enclosed space

  - Hazard: Asphyxiation if space is entered, explosion if an ignition source is introduced into the space

    - Identification:

      - Hydrogen detectors mounted high up or on the roof

      - No ventilation present in the enclosed space

    - Mitigation:

      - Ensure all areas with hydrogen storage devices and piping is well ventilated

      - Ensure an evacuation procedure is in place if hydrogen accumulation is detected

      - Ensure hydrogen detectors are placed in all high-up areas in and around locations where hydrogen is stored/used

- Use of cryogenic/liquid hydrogen

  - Hazard: Extreme cold, material embrittlement, boil-off gas

    - Identification:

      - Tanks marked with cryogenic safety signs

      - Frost buildup around tank fittings

    - Mitigation:

      - Use of gloves specifically rated for cryogenic work and a face shield is essential

      - Only use liquid hydrogen in areas with ventilation, lest the above hazards must be accounted for due to boil-off gas

https://scifleettoyota.com.au/blogDetails/Toyota-Unveils-Victoria-s-First-Hydrogen-Production-and-Re-Fuelling-Facility-Facility-at-Centre-of-Excellence/965

Creator: Joel Strickland

Copyright: Joel Strickland